## MASTER Complete
ProfileId | ProfileName | EquipmentId | EquipmentName | StatementId | StatementName | StatementContent | StatementPropertyId | StatementPropertyName | PlcFunctionId | PlcFunctionName | PlcVariable | DataType | PropertyTermId | PropertyTermName | PlcValue
1 | [6 empty] | 1 | Operation Mode | 1 | HMI | blnMA |  | 1 | Auto | 0
1 | [6 empty] | 1 | Operation Mode | 1 | HMI | blnMA |  | 2 | Manual | 1
1 | [6 empty] | 2 | MCC Trip | 1 | HMI | New Instance |  | 3 | Trip Off | 0
1 | [6 empty] | 2 | MCC Trip | 1 | HMI | New Instance |  | 4 | Trip On | 0
1 | [6 empty] | 3 | VOP | 1 | HMI | New Instance
1 | [6 empty] | 4 | Manual | 1 | HMI | blnMC |  | 5 | Start | 1
1 | [6 empty] | 4 | Manual | 1 | HMI | blnMC |  | 6 | Stop | 0
1 | [6 empty] | 5 | Trip Signal | 2 | PLC | blnTRP |  | 7 | On
1 | [6 empty] | 5 | Trip Signal | 2 | PLC | blnTRP |  | 8 | Off
1 | [6 empty] | 6 | Operation Signal | 2 | PLC | blnRUN |  | 10 | Run | 1
1 | [6 empty] | 6 | Operation Signal | 2 | PLC | blnRUN |  | 11 | Stop | 0
1 | [6 empty] | 7 | Command | 2 | PLC | blnOut |  | 12 | Run | 1
1 | [6 empty] | 7 | Command | 2 | PLC | blnOut |  | 13 | Stop | 0
1 | [6 empty] | 9 | PLC Initialize | 2 | PLC | PLCInit
1 | [6 empty] | 10 | Run Fail Timer | 3 | Delay Timer | tmrRFAL
1 | [6 empty] | 11 | Runtime recorder | 4 | Time Recorder | RFTimer
1 | [6 empty] | 12 | Trip Alarm | 1 | HMI | New Instance |  | 15 | On
1 | [6 empty] | 12 | Trip Alarm | 1 | HMI | New Instance |  | 16 | Off
1 | [6 empty] | 13 | Run Fail Alarm | 1 | HMI | New Instance |  | 17 | On
1 | [6 empty] | 13 | Run Fail Alarm | 1 | HMI | New Instance |  | 18 | Off
1 | [6 empty] | 14 | Sequence Auto | 1 | HMI | blnAUT |  | 19 | Fulfilled | 1
1 | [6 empty] | 14 | Sequence Auto | 1 | HMI | blnAUT |  | 20 | Unfulfilled | 0
1 | [6 empty] | 15 | Run Fail Buzzer | 1 | HMI | New Instance |  | 21 | On
1 | [6 empty] | 15 | Run Fail Buzzer | 1 | HMI | New Instance |  | 22 | Off
1 | [6 empty] | 16 | Trip Buzzer | 1 | HMI | New Instance |  | 23 | On
1 | [6 empty] | 16 | Trip Buzzer | 1 | HMI | New Instance |  | 24 | Off
1 | [6 empty] | 17 | HMI Acknowledge | 1 | HMI | SysAck
Yellow = to be filled in. Orange = value present but questionable.
StatementId exists in the ERD but was not exported, so every column that depends on it (StatementId, StatementName, StatementContent, EquipmentId, EquipmentName) is empty.
Fill StatementId on the StatementProperty sheet and these columns can be joined automatically.
Example row: StatementPropertyId 1 (Operation Mode) belongs to StatementId 2 (System Handle), EquipmentId 1 (Motor), DataType BOOL.

## Profile
ProfileId | ProfileName | CreatorId | IsDeleted | ClientId
1
Not supplied in the export. ProfileId 1 is referenced by Equipment and PlcFunction.

## Equipment
EquipmentId | Name | ProfileId | IsDeleted
1 | Motor | 1
2 | Valve | 1

## PlcFunction
Id | Name | ProfileId
1 | HMI | 1
2 | PLC | 1
3 | Delay Timer | 1
4 | Time Recorder | 1

## Statement
StatementId | StatementName | StatementContent | EquipmentId
1 | Operation | When auto run ready or manual run ready and no faults, then will command run. | 1
2 | System Handle | When operation mode in Auto, the Manual Start/Stop position will according with Operation Signal Run/Stop. During PLC Initialize or MCC Trip On, the Manual Operation position will be in Stop. During PLC Initialize, Run Fail Timer's delay time Set to 10 seconds. Operation Signal Run time will be recorded by runtime recorder. | 1
3 | Operation | When Manual Run Fulfilled or Auto Run Fulfilled, without trip Alarm, then PLC command Run. During motor Run, the running time will be recorded by timer recorder | 2
4 | System Handle | When in Auto Mode, Manual Operation position will change and retain according with Input Run Signal. During PLC Initializing or MCC Trip On, the Manual Operation position will be in Stop. During PLC Initializing, Run Fail Alarm Timer Setpoint assigned value 10 seconds. During PLC Initializing, Trip Alarm Timer Setpoint assigned value 3 seconds. Trip Alarm Timer will start counting when have Trip Feedback On. If the Trip Alarm Timer elapsed, Trip Alarm will turn on. Trip Alarm will off and Trip Alarm Timer will be reset when Trip Feedback is off. When Trip Alarm On, Trip Buzzer will turn on and retain. Trip Buzzer only can be reset by | 2
7 | Run Failed | When Operation signal Run not received after run fail timer elapsed, turn on Run Fail alarm, turn on Run Fail Buzzer once. When HMI Acknowledge, turn off Run Fail Buzzer | 1
11 | Auto run ready | When operation mode in Auto and Sequence Auto is fulfilled. | 1
12 | Manual run ready | When operation mode in Manual and manual started | 1
13 | Faults | When trip alarm is on or run fail alarm is on | 1
17 | Trip | When Trip Signal is On, turn on Trip Alarm, turn on Trip Buzzer once. When HMI Acknowledge, turn off Trip Buzzer. | 1

## StatementProperty
StatementPropertyId | StatementPropertyName | PlcFunctionId | StatementId | PlcVariable | DataType
1 | Operation Mode | 1 |  | blnMA
2 | MCC Trip | 1 |  | New Instance
3 | VOP | 1 |  | New Instance
4 | Manual | 1 |  | blnMC
5 | Trip Signal | 2 |  | blnTRP
6 | Operation Signal | 2 |  | blnRUN
7 | Command | 2 |  | blnOut
9 | PLC Initialize | 2 |  | PLCInit
10 | Run Fail Timer | 3 |  | tmrRFAL
11 | Runtime recorder | 4 |  | RFTimer
12 | Trip Alarm | 1 |  | New Instance
13 | Run Fail Alarm | 1 |  | New Instance
14 | Sequence Auto | 1 |  | blnAUT
15 | Run Fail Buzzer | 1 |  | New Instance
16 | Trip Buzzer | 1 |  | New Instance
17 | HMI Acknowledge | 1 |  | SysAck

## PropertyTerm
PropertyTermId | PropertyTermName | StatementPropertyId | PlcValue
1 | Auto | 1 | 0
2 | Manual | 1 | 1
3 | Trip Off | 2 | 0
4 | Trip On | 2 | 0
5 | Start | 4 | 1
6 | Stop | 4 | 0
7 | On | 5
8 | Off | 5
10 | Run | 6 | 1
11 | Stop | 6 | 0
12 | Run | 7 | 1
13 | Stop | 7 | 0
15 | On | 12
16 | Off | 12
17 | On | 13
18 | Off | 13
19 | Fulfilled | 14 | 1
20 | Unfulfilled | 14 | 0
21 | On | 15
22 | Off | 15
23 | On | 16
24 | Off | 16

## Schema Map
Child table | Child column | Parent table | Parent column | Status
Equipment | ProfileId | Profile | ProfileId | Parent table not exported
PlcFunction | ProfileId | Profile | ProfileId | Parent table not exported
Statement | EquipmentId | Equipment | EquipmentId | OK - values 1,2 resolve
StatementProperty | PlcFunctionId | PlcFunction | Id | OK - values 1-4 resolve
StatementProperty | StatementId | Statement | StatementId | MISSING - in the ERD, not in the export
PropertyTerm | StatementPropertyId | StatementProperty | StatementPropertyId | OK - all 11 values resolve
Profile
+-- Equipment --< Statement --< StatementProperty --< PropertyTerm
+-- PlcFunction ------------------^

## Data Issues
# | Severity | Where | Issue | Suggested fix
1 | Blocking | StatementProperty | StatementId is in the ERD but absent from the export - the column in its place duplicated StatementPropertyId. Without it, properties cannot be tied to statements or equipment. | Re-export with StatementId, or fill the yellow column on the StatementProperty sheet.
2 | High | StatementProperty - 6 rows | PlcVariable is the placeholder 'New Instance': MCC Trip, VOP, Trip Alarm, Run Fail Alarm, Run Fail Buzzer, Trip Buzzer. | Assign real tag names. Generated code cannot reference a placeholder and validation cannot check one.
3 | High | PropertyTerm - Ids 3 and 4 | Trip Off = 0 and Trip On = 0. Both states carry the same value. | Trip On is most likely 1. Confirm against the PLC.
4 | Medium | StatementProperty | No DataType column anywhere in the schema. The translator needs BOOL / INT / TON / TIME to choose TRUE/FALSE over 1/0 and to call timers correctly. | Add DataType to the table; a column is provided here.
5 | Medium | PropertyTerm - 10 rows | PlcValue blank for every On/Off pair (Ids 7, 8, 15-18, 21-24). | Fill in, or confirm these are BOOL where On = TRUE and Off = FALSE.
6 | Low | Profile | Both Equipment and PlcFunction reference ProfileId 1, but no Profile rows were exported. | Export the Profile table. It is 'Lipico' in the application tree.
7 | Low | Naming | The export calls it 'EquipmentType' with key 'Id'; the ERD calls it 'Equipment' with 'EquipmentId'. PropertyTerm is also called 'StatementTerm' in the export. | Align the export with the ERD so the two can be read together.